## Slide 1: ESS fire accidents & policies of Korea

## Slide 2: Status
Since 2017, More than 30 accidents occurred
Official investigations done by Government
After a few actions, ESS Fire accidents decreasing
At first, the cause of fire accidents unidentified but recently concluded as internal anomalies of batteries

## Slide 3: Safety Policy
1st safety policy(2019)
- ESS standards developed
- Regular inspection(4yr -> 1yr)
- Mandatory fire fighting equipment
2nd safety policy(2020)
- Limiting SOC(internal:80%, external: 90%)
- Saving the operating ESS data for investigating the cause of fire accidents
3rd safety policy(2022)
- SOC -> EOL : design and operate according to(or under) ‘the guaranteed life–capacity’
- Mandatory conformance certification

## Slide 4: Test center for ESS fire accidents
Building the test center for investigating ESS fire accidents
The First center for ESS in Korea
Simulation test for ESS fire accidents
Will be completed in 2022